## Slide 1: Nab SlowControl
February 2, 2025
Wolfgang Schreyer
Oak Ridge National Lab

## Slide 2: Instruments
Superconducting magnet (manufacturer software with text file logging)
Vacuum pumps & gauges (Pfeiffer, Agilent, Edwards, MKS, …)
Lakeshore temperature monitors (218, 224, 240)
Detector cooling subsystem (Legacy LabVIEW control with file logging)
Detector power subsystem (Legacy LabVIEW controls with file logging)
Fluxgates (Bartington)
Cryocoolers (Sumitomo)
Various analog and digital I/Os (NI PCIe-6323, ADAM-4000 series)
Accelerator, moderator, beamline (EPICS)
Various communication protocols (RS-232 via USB, Ethernet, RS-232 via Ethernet, RS-485 via USB, Bluetooth)

## Slide 3: SlowControl Architecture
Web server
Instrument computers
SQL SELECT
PostgreSQL database
Instrument IO service (Python)
Instrument IO thread
Database IO thread
Data queue
Command queue
Instrument hardware
Data tables
Info tables
Database clone
Public Grafana web display
Control GUIs
Control computer
Subsystem
Command thread
SQL LISTEN
SQL NOTIFY
SQL INSERT
SQL SELECT
Replication

## Slide 4: Data table structure
Column | Data type
Time (primary key) | Timestamp with timezone
Column 1 | Any type
Column 2 | Any type
… | 
Data table: data updated regularly by instrument
  Temperature, pressure, …
Config table: data that is rarely (manually) changed
  Maintains full history of configuration changes
  Update rate, channel names, …
Automatically created/expanded when instrument service starts
All tables grouped in instrument “schema”
Use time as primary key for fast time-based requests (latest entry, last 24h, a specific day, etc).

## Slide 5: Why?
LOTS of useful libraries: psycopg, pySerial, watchdog, epics, psutil, srsinst, nidaqmx, mcculw, bleak, modbus, …
Cross-platform (Windows & Linux)
Long-term support (since 1996)
Supports useful datatypes: timestamp with timezone, arrays
TimescaleDB extension optimized for time series
Open Source
Lots of different visualizations
Integrated alarm system
Why Python?
Why PostgreSQL?
Why Grafana?

## Slide 6: Some (not so) useful choices
Run instrument IO as an operating system service (see nssm for Windows)
Continuously try to reconnect in case of communication error
Run instrument IO and database IO in separate threads, buffer data in queue
Store instrument/channel assignments in timeseries table (history of configuration changes)
Central database (single point of failure) vs multiple databases (complicates backup)
No consistent table structure
Useful
Not so useful
Possible improvement: instrument IO with EPICS (caproto library), database archives EPICS variable data