## Slide 1: Improvement of emergency evacuation from underground at RIBF accelerator facility
RIKEN Nishina Center for accelerator based science Safety management group Kanenobu Tanaka

## Slide 2: RI beam factory(RIBF) in RIKEN institute
RIKEN is Japan’s largest comprehensive research institution founded in 1917 in TOKYO for high-quality research in a wide range of science.
RIBF is cyclotron facility at east area of RIKEN institute
Heavy ion beam: H ~ 238U 350 MeV/u
Goal intensity :1 particle mA (6x1012pps, 80kW in 238U beam)
In Emergency, we collect to evacuation space of large parking area
Old and new buildings are mixed. It make problem (later).
RIBF
RIKEN

## Slide 3
Escape route from underground area
Above ground: 1-4F
Underground: B1-B3F, 20m depth Complicated structure as maze !
Emergency stairs to ground
SRC(superconducting ring cyclotron)
BigRIPS（RIken projectile fragment(=RI beam) separator）

## Slide 4: 9th Nov.2015 Fire alarm activated incorrectly
Point at issue
1, Deep understanding for fire alert system
2, Improvement of alert process in an emergency
3, Improvement of self-fire brigade
a, optimization of personnel assignment
b, establish of “equipment unit” in self-fire brigade
9th/Nov./2015 Fire alarm near the SRC faraday Cup activated. Software error by radiation? All staffs should escape but it was not succeeded.
Was emergency warning not announced !? Staff A：No emergency warning was announced! Staff B：It was heard.
Different announced message with usual fire drill (usual: Check the status! / that case: Fire! Escape!)
Many people were not escaped ! <- fire announcement was not enough
Who could escape !? How dose we take a roll call?? <- Management was not enough
Some staffs told that they must enter underground to operate equipment safely !!(high voltage elec., high pressure helium gas for superconducting system)
Error alert!? Real fire!?? (How to confirm error alert)
Hydrant box
Alarm button

## Slide 5: 1, Deep understanding for fire alert system

## Slide 6: Structure of RIBF buildings and evacuation policy
Above ground：office of researcher and secretary Separated to four building
Underground ：Rad. Cont. area contain accelerators, exp. room etc. Connected each other
Fire law rule: emergency announcement should be given only to a building of fire.
RIBF case: office and exp. rooms are mixed. No one know where and when a staff exist. ->All of RIBF staffs evacuate and take a roll call !
No time difference of the emergency announcement is expected to smooth evacuation.
Linac build.
Nishina build.
RIBF acc. build.
RIBF exp. build.
4F
3F
2F
1F
B1F
B2F
B3F
B1F
B2F
B1F
B2F
3F
2F
1F
2F
1F
B1F
Side cross-sectional view of RIBF buildings
Emergency broadcasting protocol is ruled by fire protection law in Japan for large facility. (Major target: large commercial building, department store, hotel, station etc.)
Old build.
New build.

## Slide 7
Smoke detector
Fire floor (RIBF build. underground) +1 floor (RIBF build. 1F)
Phase 1 : fire alarm detector activation (smoke detection)
Emergency stairs
Linac build.
Nishina build.
RIBF acc. build.
RIBF exp. build.
Side cross-sectional view of RIBF buildings
Emergency announcement area
Old build.
New build.
Fire alarm activate ->Emergency broadcasting system start-up automatically.
Phase1:smoke detect, automatic announce only to the fire floor/+1 F/ emergency stairs, “Fire alarm activated on ○○ floor. Check the status there”
・General announcement system is inhibited.
Message and area of announcement are ruled by the fire protection law.

## Slide 8
Smoke detector
Linac build.
Nishina build.
RIBF acc. build.
phase 2: “Fire decision“ (5min. later after smoke detection)
Emergency stairs
Fire floor (RIBF build. underground) +1 floor (RIBF build. 1F)
RIBF exp. build.
Side cross-sectional view of RIBF buildings
Emergency announcement area
Alarm button
On Hydrant box
Old build.
New build.
if smoke detector was not reset for 5 min., or someone push a button of fire hydrant, the phase 1 change to “fire decision” mode
------------------------------------------------------
Phase2:“fire decision” mode, automatic announcement only to fire F/+1 F/stair ”FIRE ! Fire at ○○ floor! Escape! “ It repeat continuously.

## Slide 9
30 years old build.
Hole of emergency system. General broadcasting system exists, but Is inhibited by emergency sys. No any announcement are there.
The fire law request to announce to only to a building of fire, not to other buildings of RIBF.
Above ground: All 4 build. of RIBF were connected to emergency broadcast system.
Underground: Most of old build. were not connected to emergency sys.
19th Sep. 2015, fire alert
error occur. People in the area did not evacuate!
Phase 3: “All area announcement” (additional 5 min. later after “Fire decision“ )
Emergency announcement area
New build.
Phase3: after 5 min. of “fire decision”, (=10 min. later of initial smoke detection) announcement area expand to all area ”fire at ○○ floor! Escape!”
Message and area of announcement are ruled by the fire protection law. It can not change! But we don’t prefer this time difference.

## Slide 10
If fire alarm is activated in other old building?
①No emergency broadcasting system. Emergency bells ring inside this Nishina building only Emergency broadcasting system does not start up in all RIBF buildings. = General broadcasting system can work
Old building of 30y ago, before the current fire law start
In case of fire alarm (smoke detector) activated
Old and new facility mixed in RIKEN institute !!
Old build.
New build.
Old build.
②Central operation room of all RIKEN institute announce by general broadcast system (recorded announcement).
Staff in other building receive fire information.

## Slide 11: 2, Improvement of alert process in an emergency

## Slide 12: Manual announcement
Emergency stairs
Additional manual announcement is given from RIBF facility operation room, which have
fire information board and monitor camera. “Fire at ○○room at B2F!”
B2F
Recorded program of announcement “Fire at B2F! Escape!”
Where is fire in B2F?? But message is ruled by the fire law. No change allowed!

## Slide 13: Announce process at emergency
Phase1, only the fire floor/+1 F/emergency stairs, announced automatically “Fire alarm activated on ○○ floor. Check the status”
Phase2, “fire decision” mode, automatic announcement only to fire F/+1 F/stair ”FIRE ! Fire at ○○ floor! Escape! “
Phase3, after 5 min. of “fire decision”, announcement area change to all area ”fire at ○○ floor! Evacuate!”
1, manual announce to all RIBF buildings
“fire at ○○ room. Escape ! ”
2, Check the fire by monitoring camera
Real fire：call public firehouse
No fire seen：wait, next step
3, 12 min. after the initial fire alert
Reset the activated fire alarm, check to activate again.
4, operator+equip. unit member(later) go to alert spot of underground to check error alert or not
Given by RIBF facility operation room operator It have fire control panel, emergency sys.
Manual announcement of emer. sys. can be given only from this room.
10 min time difference to all are for evacuation announcement
emergency announcement(ruled by fire law)
By the announcement to all build., all staffs have detail information of fire spot.
If alarm is stable,
It maybe error alert.
It is useful to save
Equip. unit member (later)
Common process both for old and new buildings.
If operator have panic and mistake, auto-announcement by emergency broad. system work.
Improved (parallel process added)
Emergency
announcement is
already given to all area, staffs would be OK if the alarm stop
No change allawed by fire law in Japan
Wait 3 min. If alert was error,
the alarm will keep stable

## Slide 14
RIBF information flaw chart for fire
So far, fire drill have followed the same pattern every year!
“Fire occur in one room of all buildings, a person discover a fire”, unrealistic scenario.
Scenario was not optimized to correlate between fire brigade organization and emergency system
Problem:
1, In RIBF, “All member evacuate if other building have fire”, but it was not common sense by drills.
2, Announcement process by the emergency broadcasting system was not considered.
Fire drill and flaw chart of information
Practiced
Only this
pass at fire drill
Fire occur
Discover person
Fire alarm system
RIBF facility operation room
General broadcasting system, recorded program
Automatic emergency announcement (general announcement become inactive)
Emergency broadcast system, +Manual announcement
Central observation room

## Slide 15: 3, Improvement of self-fire brigade a, establish of “equip. unit” in self-fire brigade b, optimization of personnel assignment

## Slide 16: 3. Improvement of self-fire brigade
3-a, Equip. unit (new) When fire alarm occur, they operate equipment for safety remotely as much as possible. They are possible to approach underground to deal setups directly or to check error alert.
  For high voltage, high pressure helium gas for superconductivity, inflammable gas etc.
  Members are leader of each accelerator and experimental setups
  They collect to accel. operation room promptly at fire alert. (other workers escape to outside evacuation space)
3-b, Optimization of each unit member
  Consider their usual location of office and experimental room
  Clean up the overlap of task
  Check assignment every year

## Slide 17
A, No re-alert ->It would be error alert. Two people go underground to check status
B, Alert occur again->Real fire is possible. Wait 3 min. and check monitor camera to find fire light or smoke. If no fire sign find, error alert possible. -> case A
1, When equip. unit member receive the alert announcement, they collect to acc. operation room
2, handle equipment around the fire alert spot remotely.
Announce by hand
to all build.
Information about fire alert
location, monitoring camera etc.
3, Unit leader assign from unit member to go underground to check
Operator and equip. unit member (2 people) go to underground
with permission by unit leader
Accelerator operation room
Equipment unit of self-fire brigade
Process to approach underground to check fire alarm as safe as possible
1, fire control panel check
2, manual announce to all East area build.
“fire at ○○ room. Escape ! ”
3, Check the fire by monitoring camera
Real fire：call public fire station
No fire seen：wait, next step
4, 12 min. after the initial fire alert
Reset the activated fire alarm, check to repeat activation
Wait 3 min. If alert was error, the alarm will keep stable
RIBF facility operation room

## Slide 18: 3-b, optimization of self-fire brigade member
Important： ”Evacuation unit” and “Reporting unit”
  Evacuation unit：who usually stay office
  Reporting unit：who usually stay any room in RIBF area and can to evacuation spot
Head
Evacuation unit
(each office floor)
Reporting unit (evacuation spot)
Correct and report information of
evacuation, roll call of each build.
Office and experimental room are other building
Lot of absent worker: day or night shift operation, work at other (foreign) facility, etc.
evacuation information
of each floor
“Evacuation completed“ magnet on doors

## Slide 19: Summary for action against fire in RIBF
Design concept of emergency system for fire accident differ between old and new facility
At large facility, correlation of system and organization are important to act smoothly at emergency case.
Same scenario of fire drill every year is ineffective, easy to obsolete.
If task concentrate to a person and he busy, If a lot of cases assumed and complicated, it will not work(skipped in this slide). Simple, common process is necessary.

## Slide 20: Thank you

## Slide 21: Radioactive Isotope Beam Factory(RIBF) in RIKEN Institute
SRC（superconducting ring cyclotron）
BigRIPS（RIken projectile fragment(=RI beam) separator）
RILAC
Old facility (1981~)
New facility (2006~)
(target/beam dump)
Objects：Basic science (Nuclear phys., Nuclear astrophys., Nuclear chemistry, Radiobiology), RI production etc.
Particle: Heavy Ion beam H, O, Ca, Zn, Xe, U etc.
Energy: ~350MeV/nucleon,
Goal intensity 1 particle mA (6x1012pps, 80kW in 238U beam)
Accelerator: Superconducting Ring cyclotron (SRC)-> Most intense RI beam

## Slide 22
Escape route from underground area
Fluorescent paint guide to emergency exit
Fluorescent light
electric outage -> Emergency electric lighting system
On ground: 1-4F
Underground: B1-B3F, 20m depth Complicated structure as maze !
Emergency stairs to ground

## Slide 23
Head
First aid unit
通報連絡班長
Evacuation unit
Fire fighting unit
Evacuation magnet
check at each floor
Fire status
Roll call status
Injured status
Evacuation status
Fire emergency: self-fire brigade
Radiation safety group
Lab. supervisor
Reporting unit
Evacuation from Rad. Cont. area
“Evacuation completed“ magnet
All staffs: When they escape from a room and no one left, they put the “Evacuation completed” magnet on the outside of the door Evacuation unit: Check the magnets of all room of floor.
Fire protection law in Japan request a self-fire brigade.
In emergency, staffs collect to the evacuate space and take a roll call. So far, we have performed fire drills every year.
Radiatcion cont. area :
Roll call by the list of intakes in Rad. Cont. system
(East area： Director of
Nishina center, RIBF)

## Slide 24: Emergency broadcasting protocol is ruled by fire protection law in Japan for large facility. (Major target: large commercial building, department store, hotel etc.)
Message and area of announcement are ruled by the fire protection law. It can not change! But we don’t prefer this time difference.
Fire alarm activate (=smoke detection)->Emergency broadcasting system start-up automatically.
Phase1:smoke detect, automatic announce only to the fire floor/+1 F/ emergency stairs, “Fire alarm activated on ○○ floor. Check the status there”
・General announcement system is inhibited. ------------------------------------------------------
if smoke detector was not reset for 5 min., or someone push a button of fire hydrant, the phase 1 change to “fire decision” mode
------------------------------------------------------
Phase2:“fire decision” mode, automatic announcement only to fire F/+1 F/stair ”FIRE ! Fire at ○○ floor! Escape! “ It repeat continuously.
Phase3: after 5 min. of “fire decision”, announcement area change to all area ”fire at ○○ floor! Escape!”
9th Sep. 2015 ：started from here by software error of fire hydrant button.
It is alarm button, someone discover fire -> “fire decision mode”
Hydrant box
Smoke detector
Alarm button
Usual announcement
at fire drill every year
Different announcement

## Slide 25: Improvement of emergency broadcasting system
Fill in the hole of emergency broadcasting system
In emergency mode, announce manually from control room of RIBF (later)
Hole of emergency system, general broadcasting system exists.
Fire occur
Discover person
Fire alarm system
Central observation room
RIBF observation room
General broadcasting system, recorded program
Automatic emergency announcement (general announcement inactive)
Emergency broadcast system, Manual announcement
Emergency announcement area