## Slide 1
Pre-defined safety measures for helium leakages – theory meets reality
by Sven Mohr
DESY
Department Safety and Environmental Protection

## Slide 2
structure
Experiences at DESY
Early planning XFEL
Iteration planning
Current situation

## Slide 3
Experiences @DESY
Simulation of dispersion processes
2 tests 18.02.1989 (10:11:00)
2 x 500l (≈ 125 kg) liquid Helium in HERA tunnel (6.3km circumference, 5.2m diameter)
Assumptions for the critical case: 120kg in 10s
Hazards: suffocation caused by oxygen deficiency and frostbite
→ focus on safety (of people): technical/organizational measures? PPE?

## Slide 4
Experiences @DESY
Framework:
60 probes for temperature and oxygen level
Activated ventilation system
Test areas 20m/100m against and 100m/200m in the direction of ventilation path
Release in 2,5m/1m height

## Slide 5
Experiences @DESY - Welcome to the 80ies!

## Slide 6
Experiences @DESY - results 1st test
Gas rises to ridge immediately
Almost no mixing with tunnel air
Fast spreading
Spreading against tunnel ventilation

## Slide 7
Experiences @DESY - results 2nd test
More mixing with tunnel air
Slower spreading (> tunnel ventilation)
→ cold temperatures > oxygen deficiency
→ no stationary oxygen level monitoring
→ no self-rescue devices

## Slide 8
Early planning XFEL
Measures (as required in plan approval order)
Openings in fire compartment separations remain open
Helium release through shaft buildings
Activation of smoke extraction duct
Opening of nearest flaps
Performance level of smoke extraction system 23.000 m3/h (tunnel volume ≈ 46.000m3, ≈ 24.000m3 free of installations - editor´s note)
Source: STUVA safety expertise, 2005

## Slide 9
Early planning XFEL
Everything changed
Internal approaches reviewed
Legal requirements questioned
Alternative technical solutions to be found
→ additional focus on machine safety

## Slide 10
Early planning XFEL - open questions
Activation/reaction time of smoke extraction duct?
Flaps still operative in supercool range?
Can duct manage volume flow in worse/worst cases?
Can the main escape routes (staircases) be kept clear?
Source: Wroclaw University of Technology, Report on the risk analysis of the XFEL-Linac cryogenic system

## Slide 11
Iteration planning - existing infrastructure
Design changes in smoke extraction system:
Smoke extraction duct cancelled (→ maintenence, space)
As a result no flaps
Longitudinal smoke extraction through tunnel structure

## Slide 12
Iteration planning - existing infrastructure
Design changes in suspensions / cryo system:
Reinforced suspensions for cryo installations
Customized overpressure protection
Focus on cool down and warm up phases (bigger Helium mass in intermediate states)

## Slide 13
Iteration planning
Measures:
Openings in fire compartment separations remain open
Helium release through shaft buildings
Activation of smoke extraction duct
Opening of nearest flaps
Performance level of smoke extraction system 23.000 m3/h


X
X


## Slide 14
Current situation - temporary solution
Temporary solution needed for cool down and operating phases:
→ Safety measures for massive helium leakage by Fabian Saretzki

## Slide 15
Sven Mohr Coordination XFEL Work package 36 - General Safety Deutsches Elektronen-Synchrotron D5 - Arbeitssicherheit/Umweltschutz Notkestraße 85, Gebäude 35 22607 Hamburg Tel.: +49 40 8998 - 4831 Fax.: +49 40 8998 - 4311 Mobil: +49 175 2619881 Mail: sven.mohr@desy.de