## Slide 2: FRPAM a Fire Response Probabilistic Analysis Model
A. Andreini, O. Rios, S. La Mendola, A. Arnalich – CERN, HSE-SEE-XP
International Technical Safety Forum
ITSF 2017
September 18-22, 2017
TRIUMF, Vancouver Canada

## Slide 3: FRPAM a Fire Response Probabilistic Analysis Model
Joint effort of CERN Fire Safety Engineering Team
Early stage of development
Limited to CERN though easy to outstretch
Additional validation needed, yet encouraging results

## Slide 4: FRPAM
FRPAM is a probabilistic tool to assess the fire response of a complex facility.

## Slide 5: FRPAM
CERN
FIRE BRIGADE
FIREFIGHTING TRAIN
SPRINKLER
FFFS
FRPAM is a probabilistic tool to assess the fire response of a complex facility.
MINOS detector, Fermilab
LHC tunnel and TIM, CERN

## Slide 6: FRPAM
FRPAM is a probabilistic tool to assess the fire response of a complex facility.
  Response time of crews (tresponse)
    tresponse= tdetection + ttournout + tblock+ ttravel + taccess
  Time to extinguish fire (textinguish)
    textinguish = tresponse+ tknockdown
  Total energy release (Etotal)
      Etotal =
MEDICAL SUPPORT
EVACUATION SEARCH& RESCUE
FIRE CONDITIONS
PROPERTY DAMAGE

## Slide 7: FRPAM
FRPAM is a probabilistic tool to assess the fire response of a complex facility.
CDF
time
1
Pi
xi
CDF (Cumulative Distribution Function)
Probability of extiguishing the fire under a given time lapse or energy release.
90%
75m

## Slide 8: FRPAM
FRPAM is a probabilistic tool to assess the fire response of a complex facility.
CDF
energy release
1
Pi
xi
CDF (Cumulative Distribution Function)
Probability of extiguishing the fire under a given time lapse or energy release.
90%
50GJ

## Slide 9: Trial Design benchmark

## Slide 10: Trial Design benchmark
SCENARIO
FIRE RESPONSE
FIRE BRIGADE
DESIGN FIRE
TRIAL DESIGN
#1
SCENARIO
FIRE RESPONSE
FIRE BRIGADE
DESIGN FIRE
TRIAL DESIGN
#2
ROBOT

## Slide 11: Trial Design benchmark
CDF
energy release
1
90%
50GJ
36GJ
CDF
1
90%
75m
35m
time
TRIAL DESIGN #1
TRIAL DESIGN #2
For 90% of the cases, fire extinction is achieved within 75’ and a 36GJ energy release in TD#1 versus 35’ and 50GJ in TD#2.
TRIAL DESIGN #1
TRIAL DESIGN #2

## Slide 12: Model architecture
ttournout
time
fire ignition
fire detected
sprinkler triggered
crews dispatched
crews at surface
robot attack
crews seat of fire
fire extinguished
Turnout
Travel
Access
Manual
firefighting
Detection
tdetection
ttravel
taccess
tknockdown
tresponse
Sprinkler activation
Sprinkler action
Robot travel
Robot
action
textinguish

## Slide 13: Model architecture
  Monte-Carlo method to build histograms and CDFs (LatinHypercube sampling with preservation of correlation matrix)
All submodels into a Python script
Multiple (1000) simulations/run
Time steps t=0.05s

## Slide 14
Turnout
Travel
Access
Manual
firefighting
Detection
PDF
t
Fire Detection Distribution ~2%
Gamma distribution
From fire ignition to fire notification
Standard gamma distribution model
Calibration with CERN fire detection system specifications
Potential implementation of a fully developed probabilistic model by Joglar et al. Fire Technology (2005)

## Slide 15
Turnout
Travel
Access
Manual
firefighting
Detection
From fire notification to crews leaving station
Standard gamma distribution model - Tillander, K. VTT (2004)
Calibration with CERN Fire Brigade estimates, additional data aquisition needed
Turnout Distribution ~4%

## Slide 16
Turnout
Travel
Access
Manual
firefighting
Detection
From crews leaving station to access building
Tested travel model for NYC – Kolesar et al. (1975)
Found fit and adjusted with statistical data in Finland - Tillander, K. VTT (2004)
Travel Submodel ~25%
t is travel time
d is distance
a, b ,c are model parameters
Statistical uncertainties for a, b, and c

## Slide 17
Turnout
Travel
Access
Manual
firefighting
Detection
From access building to seat of the fire
Access Submodel ~25-50%
Access point in surface
Seat of the fire

## Slide 18
Turnout
Travel
Access
Manual
firefighting
Detection
From access building to seat of the fire
Travel speed and obstacle bypass time model
Adjusted with data from CERN Fire Brigade drills
All parameters (14) introduced as probabilistic variables
Good performance, but limited sample
Additional CERN Fire Brigade drills foreseen
Access Submodel ~25-50%

## Slide 19
Turnout
Travel
Access
Manual
firefighting
Detection
From seat of the fire to fire knockdown
Proposed model is HRR dependent
Includes defensive approaches when HRR > HRRcritical
Manual firefighting Submodel ~2-50%
time
HRR
HRRcritical
HRRcritical and are probabilistic distributions
= 20 MW based on firefighting water flowrate - Barnett, C. SFPE NZ (2004)
is adjusted to fit experimental data

## Slide 20
Time of activation ts computed every time step using Alpert’s correlations and assuming quasi-static fire.
Sprinkler activation
Sprinkler activation
Sprinkler action
Time of activation:
Gas temperature:
Gas velocity:
Notes: Where:
  RTI is the Response Time Index RTI to be provided by supplier but a value of 90 can be taken
  is the design temperature to activate the sprinkler (68ºC),
  is ambient temperature
  and the gas velocity () and its temperature () are calculated according to the is the convective part of the fire
  is the longitudinal distance from the sprinkler head to the fire (assumed 1.5m)
  is the height to the fire (assumed 3m)
The orange line in the plot is the activation time for different HRR considering TUNNEL equations.. however, I don't implemented them 'cause we have to considere a ventilation value... and I didn't want to input this... orange is calculated with U=0.5m/s
Where:
  RTI is the Response Time Index RTI to be provided by supplier but a value of 90 can be taken
  𝑇_𝑑is the design temperature to activate the sprinkler (68ºC),
  𝑇_𝑜 is ambient temperature
  and the gas velocity (𝑢_𝑔) and its temperature (𝑇_𝑔) are calculated according to the 𝑋𝑐=2/3 is the convective part of the fire
  𝑥 is the longitudinal distance from the sprinkler head to the fire (assumed 1.5m)
  𝐻 is the height to the fire (assumed 3m)

## Slide 21
As proposed in the Swedish construction code – §3.3.5 BBRAD
Sprinkler action
Sprinkler activation
Sprinkler action
Heat Release Rate:
Notes: If
If
Where:
  is the HRR at sprinkler activation time ts
If 𝒒 ̇(𝒕_𝒔 )=(𝒒_𝒔 ) ̇<𝟓𝑴𝑾 {■8((𝑞_𝑠 ) ̇(𝑡)=(𝑞_𝑠 ) ̇−(((𝑞_𝑠 ) ̇−(𝑞_𝑠 ) ̇/3)/60)·𝑡=(𝑞_𝑠 ) ̇−(𝑞_𝑠 ) ̇/90·𝑡 → 𝑓𝑜𝑟 𝑡≤𝑡_𝑠+60𝑠 @(𝒒_𝒔 ) ̇(𝒕)=(𝒒_𝒔 ) ̇/𝟑 → 𝑓𝑜𝑟 𝑡>𝑡_𝑠+60𝑠)}
If 𝒒 ̇(𝒕_𝒔 )=(𝒒_𝒔 ) ̇>𝟓𝑴𝑾 (𝑞_𝑠 ) ̇(𝑡)=(𝑞_𝑠 ) ̇
Where:
  (𝑞_𝑠 ) ̇ is the HRR at sprinkler activation time ts

## Slide 22
Multiple aerosol generators (K based)
Non-toxic, electronic safe
Firefighting robot
Robot travel
Robot
action

## Slide 23
Multiple aerosol generators (K based)
Non-toxic, electronic safe
Achieves total supression for limited time, then fire rekindles with a reduced growth rate assuming a ventilation speed.
Firefighting robot
Robot travel
Robot
action
Heat Release Rate:
Time of arrival:
Supression time lapse:

## Slide 24: Trials – Scenario
AWAKE – TSG4
Access point in surface
Seat of the fire
EXAMPLE FOR BB4 to fire in TSG4 (AWAKE) |  |  |  | 
Quantity | Description | vi / Tj | Unit | Time (min)
58.5 | descending stairs | 11.70 | m/min | 5.00
0 | ascending stairs | 10.00 | m/min | 0.00
0 | descending elevator travel | 12.00 | m/min | 0.00
0 | ascending elevator travel | 12.00 | m/min | 0.00
0 | horizontal travel w/ visibility | 83.33 | m/min | 0.00
0 | horizontal travel wo/ visibility | 49.25 | m/min | 0.00
800 | horizontal travel on fire trailer | 133.33 | m/min | 6.00
80 | hose deployment | 18.48 | m/min | 4.33
1 | PAD-MAD access | 6.00 | min/unit | 6.00
1 | access door | 0.50 | min/unit | 0.50
3 | closed ventilation/fire door | 0.50 | min/unit | 1.50
1 | fire trailer setup | 4.50 | min/unit | 4.50
1 | hose line hook up and water | 4.00 | min/unit | 4.00
1 | team gear up on air | 1.50 | min/unit | 1.50

## Slide 25: Trials – Design fires
# | HRRmax [MW] | delt1 [min] | delt2 [min]
1 | 30 | 15 | 45
2 | 18 | 15 | 45
3 | 5 | 15 | 45

## Slide 26: Trials – Fire response
# | RESOURCES
FF | FIRE BRIGADE (*)
FF+TIM | FIRE BRIGADE (*) ROBOT
FF+2TIM | FIRE BRIGADE (*) 2 * ROBOT
FF+SPKL | FIRE BRIGADE (*) SPRINKLER
(*) Standard CERN FB response (7 firefighter + 1 crew commander + 1 officer)

## Slide 27: Time to extinguish fire textinguish Case #1 - Design fire 30MW
FB
FB
SPRINKLER
FB
ROBOT
75m
@90%
44m
@90%
68m
@90%

## Slide 28: Total energy release Etotal Case #1 - Design fire 30MW
FB
FB
SPRINKLER
FB
ROBOT
115GJ@90%
1GJ
@90%
55GJ
@90%

## Slide 29: Roadmap
Submodel for Fire Brigade block
Two seats of the fire (cable trays)
Validation (full and individual models)
    Additional data (access model)
    Manual firefighting model Suppression model